OUTSIDE HUMIDITY/TEMPERATURE TRANSMITTER

HTOS Series

The HTDT series incorporates:

- Highly Accurate RH Sensing Element

- Choice of analog outputs

- Precision Platinum RTD for Temperature

- Polycarbonate weatherproof enclosure

- AC/DC operation

PRODUCT HIGHLIGHTS

- Humidity range: 0-100%

- Accuracy available 2%, 3%, & 5%

SPECIFICATIONS

| SPECIFICATIONS |  |
| --- | --- |
| HUMIDITY SENSOR TYPE | Thermoset polymer based capacitive |
| TEMPERATURE SENSOR TYPE | 1000Ω Platinum, IEC 751, 385 Alpha, thin film |
| HUMIDITY SENSOR ACCURACY | ±2, 3, or 5 %RH (5 to 95 %RH) |
| TEMPERATURE SENSOR ACCURACY | ±0.1% of span |
| SENSOR RESPONSE TIME | 15 seconds typical |
| MEASUREMENT RANGE | 0 to 100 %RH |
| HYSTERESIS | ±1.5 %RH maximum |
| REPEATABILITY | ±0.5 %RH typical |
| OPERATING TEMPERATURE | -40 to 50°C (-40 to 122°F) |
| OPERATING HUMIDITY | 0 to 95 %RH non-condensing |
| POWER SUPPLY | 24 Vac/Vdc, +/- 10% |
| CONSUMPTION | 22 mA maximum |
| INPUT VOLTAGE EFFECT | Negligible over specified operating range |
| PROTECTION CIRCUITRY | Reverse voltage protected and output limited |
| OUTPUT SIGNAL | 4-20 mA, 0-5 Vdc, or 0-10 Vdc (factory configured) |
| OUTPUT DRIVE @ 24 VDC | Current: 550Ω max Voltage: 10,000Ω min |
| INTERNAL ADJUSTMENTS | Clearly marked ZERO and SPAN pots |
| ENCLOSURE | Polycarbonate, UL94-V0, IP65 (NEMA 4X) |
| TERMINATION | Screw terminal block (14 to 22 AWG) |
| COUNTRY OF ORIGIN | Canada |