SPLIT-CORE AC CURRENT SENSOR

SC-650 Series

The SC-650 series incorporates:

- split-core design

- self-powered and no insertion loss

- 0-5 Vdc Output

- average measurement

- solid-state reliability

- input / output isolation via current transformer

PRODUCT HIGHLIGHTS

- compact form factor

- solid, reliable mounting

SPECIFICATIONS

| SPECIFICATIONS |  |
| --- | --- |
| MEASUREMENT RANGE | SC-650-R1: 0-10/20/50 Amps SC-650-R2: 0-50/10/150 Amps SC-650-R2: 0-50/10/150 Amps |
| MAXIMUM INPUT CURRENT | SC-650-R1: 100 Amps continuous SC-650-R2: 150 Amps continuous SC-650-200: 250 Amps continuous |
| ACCURACY | SC-650-R1/R2: ±2% FSO, SC-650-200: ±1% FSO (5-100% of range) |
| SIGNAL | 0-5 Vdc |
| SENSOR POWER | Self-powered |
| INSULATION CLASS | 600 Vac, insulated conductors |
| FREQUENCY | 50/60 Hz |
| RESPONSE TIME | 200 mS typical, 0-90% |
| OUTPUT LOAD | 1 MΩ typical |
| LOADING ERROR | Add 0.5% error with 100KΩ |
| OPERATING TEMPERATURE | -15 to 60°C (5 to 140°F) |
| OPERATING HUMIDITY | 5 to 90 %RH non-condensing |
| TERMINAL BLOCK | 14 to 22 AWG |
| DIMENSIONS | 76mm W x 79mm H x 24.9mm D (3” x 3.1” x 0.98”) |
| SENSOR APERTURE | 20.3mm (0.8”) |
| ENCLOSURE MATERIAL | ABS/PC, UL94-V0 |
| AGENCY APPROVALS | cULus listed |