OUTSIDE DEWPOINT TRANSMITTER

DWOS SERIES

The outside dewpoint transmitters are designed for use in environmental monitoring and control systems where high performance and stability are demanded. It’s state-of-the-art design combines digital linearization and temperature compensation with a highly accurate and reliable humidity sensor and curve-matched NTC thermistor temperature sensor for reliability and accuracy in the most critical applications.

The dewpoint series has four measurement variables which include dewpoint, dry-bulb temperature, wet-bulb temperature and enthalpy which are available by either an analog, BACnet® or Modbus signal to provide the most efficient monitoring and control solution. A hinged and gasketed, weatherproof Polycarbonate enclosure is included for ease of installation.

PRODUCT HIGHLIGHTS

- Measures dewpoint, dry-bulb temperature, wet-bulb temperature and enthalpy.

- Analog output types field selectable 4-20mA or Voltage

- Analog outputs: Dewpoint Temperature, Wet Bulb Temperature or Enthalpy (field selectable)

- BACnet or Modbus communication, factory configurable.

- Weatherproof Polycarbonate enclosure

ENGINEERING SPEC’S

- Shall be IP65 (NEMA 4X) with a UL94-V0 rated enclosure

- External mounting tabs must be slotted & tapered away from enclosure to ease field installation

- Enclosure shall be complete with neoprene gasket for duct to enclosure seal

- Enclosure shall be complete with threaded (1/2 NPT and/or M16) conduit connection

- Cover must be hinged and securely attached in the open position

- Operating range must be -30 to 50°C (-22 to 122°F), 0 to 95 %RH non-condensing

- Cover must contain security screw as extra protection from opening

- Product shall be CE approved

SPECIFICATIONS

| DESCRIPTION | ENGINEERING SPEC |
| --- | --- |
| MEASUREMENT RANGE | Relative Humidity: 0 to 100 %RH Dry Bulb Temperature: -30 to 50°C (-22 to 122°F) |
| CALCULATED VALUES | Dewpoint Temperature: -30 to 50°C (-22 to 122°F) Wet Bulb Temperature: -30 to 50°C (-22 to 122°F) Enthalpy: 0 to 340 kJ/kg (0 to 146 BTU/lb) |
| ACCURACY | Relative Humidity (RH): ±2 %RH, 10 to 90 %RH @ 25°C Dry Bulb Temperature (T): ±0.2°C (±0.4°F) @ 0 to 50°C (32 to 122°F) Dewpoint Temperature (Td): ±1.0°C (±1.8°F) @ 40 %RH / 25°C Wet Bulb Temperature (Tw): ±1.0°C (±1.8°F) @ 50 %RH / 25°C Enthalpy: ±2 kJ/kg (±1 BTU/lb) @ 50 %RH / 25°C |
| LCD DISPLAY VALUES | Temperature: -30.0 to 50.0°C (0.5°C resolution) or -22 to 122°F (1°F resolution) Dewpoint: -30.0 to 50.0°C Td (0.5°C resolution) or -22 to 122°F Td (1°F resolution) Wet Bulb: -20.0 to 50.0°C Tw (0.5°C resolution) or -4 to 122°F Tw (1°F resolution) Enthalpy: 0 to 340 kJ/kg (1 kJ/kg resolution or 0 to 146 BTU/lb (1BTU/lb resolution) |
| OUTPUT | Signals (2X): 4-20 mA or 0-5/0-10 Vdc (factory set) Signal 1 and 2: Dewpoint Temperature, Wet Bulb Temperature or Enthalpy (field selectable) - Td Range 1: -30 to 50°C (-22 to 122°F) - Td Range 2: -20 to 40°C (-4 to 104°F) - Td Range 3: 0 to 50°C (32 to 122°F) - Tw Range 1: -20 to 50°C (-4 to 122°F) - Tw Range 2: 0 to 50°C (32 to 122°F) - En Range 1: 0 to 340 kJ/kg (0 to 146 BTU/lb) - En Range 2: 0 to 250 kJ/kg (0 to 107 BTU/lb) Impedance @ 24 Vdc: Current: 500Ω max Voltage: 10,0000Ω minimum |
| BACnet® PROTOCOL | MS/TP, 2-wire RS-485 Baud rate - 9600, 19200, 38400, 57600, or 115200 0-127 slave address range |
| MODBUS PROTOCOL | RTU, 2-wire RS-485 Baud rate - 300, 600, 1200, 2400, 4800, 9600, 19200, or 38400 1-255 slave address range |
| POWER SUPPLY | 20 to 27 Vdc, 16 to 27 Vac (non-isolated half-wave rectified) |
| CONSUMPTION @ 24 VAC | Current: 50 mA max @ 24 Vdc, 1.5 VA max Voltage: 30 mA max @ 24 Vdc, 1 VA @ 24 Vac |
| OPERATING CONDITIONS | -30 to 50°C (-22 to 122°F), 0 to 95 %RH non-condensing |
| STORAGE CONDITIONS | -40 to 70°C (-40 to 158°F), 0 to 95 %RH non-condensing |
| WIRING CONNECTIONS | Terminal block (14 to 22 AWG) |
| ENCLOSURE | Material: B - Grey polycarbonate, UL94-V0, IP65 (NEMA 4X) F - Same as B, includes thread adapter (1/2” NPT to M16) and cable gland fitting Dimensions: 112.5mm W x 116.5mm H x 53.7mm D (4.43” x 4.58” 2.11”) Probe: 230mm (9”) L x 12.7mm (1/2”) D, 304 S/S with porous filter |
| APPROVALS | CE |
| COUNTRY OF ORIGIN | Canada |